## Slide 1: Introduction to Nutrient Optimization
Nicholas Willis
Environmental Finance Center at Wichita State
Grant Weaver, Grant Tech Solutions
Tom Stiles, KDHE W

## Slide 2: Nutrient Optimization Webinar Series
Series of Five Webinars
November 8, 2023 Introduction to Optimizing Wastewater Treatment Plant Performance
November 15, 2023 Kansas Nutrient Optimization Case Studies
November 29, 2023 Nitrogen Removal Concepts
December 6, 2023 Phosphorus Removal Concepts
December 13, 2023 Review of Nutrient Optimization Concepts
1.5 CEUs per session wastewater operator credit

## Slide 3: Who’s this guy?
Environmental Finance Center at Wichita State University
  Nutrient optimization and jar testing – over 90 plants
  Asset management, rates and finance training and technical assistance
Assistant Utility Director – Hays, KS
  Four budgets, two plants, levee, limited water, bad drought, conservation
NPDES Permit Writer, State of Arkansas
Biosystems Engineering – University of Neb-Lincoln. Registered P.E. - Kansas

## Slide 4: Who’s the other guy?
Grant Tech, Inc.
  In-plant support for optimizing nutrient removal in 175+ municipal wastewater treatment plants including 73 in Kansas
Wastewater Operator
  Connecticut
  Massachusetts
  New Hampshire
  Rhode Island
Professional Engineer
  Connecticut
MIT: Post-Grad Studies in Environmental Toxicology
Oklahoma State: MS Bio-Environmental Engineering
Kansas State: BS Biology

## Slide 5: KDHE Perspective

## Slide 6: KDHE Perspective on Optimization for Nutrients
Chart: El Dorado Wastewater TP


Chart: El Dorado Wastewater TP Loads (#/d)
Rolling Avg TP | 6.5096 | 6.4844 | 6.2097 | 5.8292 | 5.3121 | 4.5368 | 4.0925 | 4.1927 | 3.4522 | 3.4844 | 3.5666 | 3.6438 | 3.5814 | 3.2054 | 3.193 | 4.0768 | 5.374 | 6.3123 | 7.1905 | 7.4939 | 7.1859 | 7.1743 | 7.1892 | 7.2234 | 7.5434 | 7.6812 | 12.6186 | 11.9223 | 10.5684 | 9.9266 | 9.4062 | 8.6637 | 8.5623 | 8.4443 | 8.3743 | 8.3064 | 8.1338 | 8.2959 | 3.1883 | 3.2972 | 4.095 | 3.8572 | 5.627 | 5.5387 | 5.7393 | 5.9816 | 6.0149 | 6.0763 | 5.9399 | 5.7344 | 5.3375 | 5.7935 | 5.2995

## Slide 7: What’s the issue with nutrients?

## Slide 8: Ecosystem Productivity
All ecosystems having limiting factors to their productivity:
Deserts – water
Corn fields – typically nitrogen, phosphorus or water
Soybean fields – typically pH, phosphorus or water
Tundra – sunlight, temperature
Freshwater – typically phosphorus
Salt water – typically nitrogen
Activated sludge treatment – dissolved oxygen, pH, time

## Slide 9: Total Nitrogen
If ammonia is removed – converted to nitrates
  Ammonia removal preserves nearby aquatic life
Nitrates are problematic:
  Maximum Contaminant Level under Safe Drinking Water Act
  Brackish and salt-water eutrophication
    Gulf of Mexico Dead Zone

## Slide 10
From the National Oceanic and Atmospheric Administration

## Slide 11
From: The Advocate (Louisiana Newspaper). 'Large to very large' Gulf of Mexico dead zone expected this year; Here's what caused it May 16, 2019

## Slide 12: Total Phosphorus
Excess phosphorus increases freshwater biomass production
Similar to dead zone in Gulf of Mexico – increases algae production
Excessive algae a problem:
  Can be toxic – Harmful Algal Blooms
  Shades lower parts of lake
  Taste & Odor Issues
  May close recreation
  May impact drinking water treatment
  Fish kills may occur

## Slide 13: Where is phosphorous coming from?
People
  Dominates WWTP
  Anyone with a bottle of soda?
  Read the ingredient list
  Common food preservative
Detergents
  Minor contributor at this point
Fertilizers
Animal wastes
  Added to hog & dairy feed
Notes: Humans excrete about 3.3 million tons of phosphorous annually
A UK study showed that about 70% of phosphorous in wastewater was from feces and urine

## Slide 14: Industrial sources
Food & beverage processing
  Waste products
  Cleaning products
  Preservatives
Fertilizer Production
Metal finishing
  Cleaning
Hesston, KS

## Slide 15: Nutrient Regulation in Kansas

## Slide 16: Kansas Nutrient Regulations
Most facilities can expect:
  Mass-based limits calculated off plant design-flows at:
  10.0 mg/l Total Nitrogen
  1.0 mg/l Total Phosphorus
  Typically Rolling Annual Averages
  Some facilities will get:
    Hard limits for total nitrogen or nitrates (drinking water MCL)
    More stringent phosphorus limits (TMDL driven)

## Slide 17: What does this mean?
Mass-based limits
  Can discharge higher than concentration based limit
  i.e. if plant design is 1.0 MGD and you average 0.5 MGD, concentration can effectively double and be in mass-based compliance
Rolling Annual Average
  Allowed to exceed limits if offset by performance better than limits in other months
  One bad month can cause months of non-compliance
  Sample early – repeat if high to reduce monthly average
    i.e. if TP comes back at 5.2 mg/l, sample again to reduce monthly average

## Slide 18: Nutrient Optimization

## Slide 19: Utility Sustainability
Wastewater systems face numerous pressures:
Collection System Investment Needs
Aging Infrastructure
Equipment Supply Chain
Emerging contaminants – i.e. PFAS/PFOS
Stagnant/declining populations
ALL pressure utility finances

## Slide 20: Nutrient Optimization Benefits Utility Finances
Reduce energy usage
Reduce chemical usage
Alum/ferric for phosphorus
Alkalinity addition for denitrification (rare in KS)
Eliminate or Delay Need for Capital Investment
Resource availability for collection systems

## Slide 21: Theory of Nutrient Optimization
Operators can operate differently than plant design
Nutrient removal is all about:
  Having the right environments
  In the right places
  At the right times
Biological Nutrient Removal Plants do this by design
Other plants do it with creativity and operator skill

## Slide 22: Environments for Nitrogen Removal
Two-steps (in most plants)
Aerobic – convert ammonia to nitrates
  ~6 hours for conversion
Anoxic – convert nitrate to nitrogen gas
  ~1-2 hours for conversion
  Need BOD or added carbon

## Slide 23: Environments for Phosphorus Removal
Volatile Fatty Acid Production
  Anaerobic with carbon
  Typically influent + Return Activated Sludge
Bio-P consume VFA
  Anaerobic with carbon (typically same tank as fermentation)
  Phosphorus Release occurs
Phosphorus Uptake
  Aerobic environment

## Slide 24: What does this look like?
Image from Shengan Xu, 2014

## Slide 25: Optimization Versus Design
Your plant optimized for nutrient removal will not look like the plant on the right.
That’s OK
You need the environments – not the tanks

## Slide 26: Total Nitrogen Removal
Two Step Process
Step 1: Convert Ammonia to Nitrates
Step 2: Convert Nitrates to Nitrogen gas

## Slide 27: Conversion of Ammonia (NH4)
Nearly all nitrogen entering municipal plants is in ammonia form
  Toxic to aquatic life
  Needs removed
  NO3 is product – stays in water
    Drinking water professionals – this can be a problem – MCL of 10.0 mg/l
“Nitrifiers” are responsible for conversion of ammonia to nitrates
  Energy derived from oxidizing inorganic nitrogen compounds (ammonia)
  Aerobic environment – Oxygen Rich
  pH and temperature sensitive bacteria
    Functionally, most NE plants will struggle with temperature, pH should be fine with most hard waters
  Two-step process
    Ammonia oxidized to nitrite (NO2) then nitrite oxidized to nitrate (NO3)
    Very little nitrite is seen in wastewater discharges

## Slide 28
Ammonia (NH4)
Ammonia Removal
Ammonia (NH4) is converted to Nitrate (NO3)
Animation from Grant Weaver

## Slide 29: Ammonia Removal
Ammonia (NH4)
Oxygen (O2)
Animation from Grant Weaver

## Slide 30: Ammonia Removal
Ammonia (NH4)
Alkalinity
Oxygen (O2)
H+
Animation from Grant Weaver

## Slide 31: Ammonia Removal
Ammonia (NH4)
Nitrite (NO2)
Alkalinity
Oxygen (O2)
H+
Animation from Grant Weaver

## Slide 32: Ammonia Removal
Ammonia (NH4)
Nitrite (NO2)
Alkalinity
Oxygen (O2)
Oxygen (O2)
H+
Animation from Grant Weaver

## Slide 33: Ammonia Removal
Ammonia (NH4)
Nitrite (NO2)
Nitrate (NO3)
Alkalinity
Oxygen (O2)
Oxygen (O2)
H+
Animation from Grant Weaver

## Slide 34: Nitrate conversion to nitrogen gas
For conversion, the following is needed:
Low/no dissolved oxygen
Carbon source
Typically influent BOD, some plants add
Regain half of lost alkalinity

## Slide 36: Benefits of Nitrate Removal
Improved water quality
Gulf of Mexico & Drinking Water Quality
Energy savings
Cycle aeration or turn off part of aeration
Control D.O. with D.O. feedback

## Slide 37: Total Phosphorus
3 Steps

## Slide 38: Step 1: Produce Volatile Fatty Acids
Ingredients:
Mixed liquor solids, low in nitrates
Influent rich in carbon
Time: 1 to 2ish hours
Directions – allow to ferment
Minimal mixing, no/minimal air introduction
Oxidation Reduction Potential = -100 to -250 mV

## Slide 39: Step 2: Bio-P uptake VFA
Directions:
This occurs, typically in same basin as VFA production
Prevent nitrates, as denitrifying bacteria consume VFA
Check your work:
Phosphate levels should be 3x influent leaving basin as influent
Oxidation Reduction Potential = -100 to -250 mV

## Slide 40: Step 3:
Direct fluid rich in Bio-P bugs, fat with VFA, into aerobic basin
“Luxury” phosphorus uptake occurs
Remove in solids
Operate clarifier and biosolids to minimize phosphorus release

## Slide 42: Phosphorus – Common Failure Points
Nitrates entering “Anaerobic Zone”
  Return Activated Sludge
High Dissolved Oxygen in “Anaerobic Zone”
  Return Activated Sludge
  Backflows
  Overmixing
Release from sludge
  Deep clarifier blankets
  Sludge processing

## Slide 43: Sunapee, NH
Total Nitrogen
  Ditches operate in parallel
  TN Removed in ditches – rotors cycle on/off
    Aerobic to Anoxic
  Dissolved Oxygen setpoints for rotors
Total Phosphorus
  Two parallel anaerobic basins
  Overmixed – reduce mixing time
  Protect from washout?
All aerials in presentation from Google Earth unless otherwise specified.

## Slide 44: Sunapee, NH
Solids handling
  Dose Polyaluminum Chloride (PAC) with polymer before belt press
  Binds phosphorus released during solids storage – remain in solids
Adaptive Operations
  Test phosphate leaving ditches. Monitor Anaerobic Basin Oxidation Reduction Potential values
  Plan A: Anaerobic zones
  Plan A.1: PAC during solids processing
  Plan B: Chemical before clarifiers
  Plan B.1: PAC during solids processing

## Slide 47
Chart: Effluent total-Phosphorus (mg/L) Great Bend, Kansas
| Jan19 | F19 | M19 | A19 | M19 | J19 | July | A19 | S19 | O19 | N19 | D19 | Jan20 | F20 | M20 | A20 | M20 | J20 | July | A20 | S20 | O20 | N20 | D20 | Jan21 | F21 | M21 | A21 | M21 | J21 | July | A21 | S21 | O21 | N21 | D21 | Jan22 | F22 | M22 | A22 | M22 | J22 | July | A22 | S22 | O22 | N22 | D22
total-P | 2.5 | 1.2 | 3.38 | 2.5 | 1.7 | 1.2 | 1.3 | 2.1 | 2.9 | 2.7 | 2.1 | 2.1 | 2.6 | 2.3 | 2.2 | 2.4 | 3.5 | 2.8 | 3.3 | 2.7 | 1.2 | 0.85 | 0.34 | 0.26 | 0.85 | 0.27 | 0.41 | 1.4 | 0.14 | 0 | 0.16 | 0.4 | 0.12 | 1.2 | 0.6 | 0.18 | 0.36 | 0.75 | 1.2 | 0.31 | 1.4 | 0.47 | 0.43 | 2.38 | 0.55 | 0.63 | 0.4 | 0.8
Rolling 12-mo AVG | 3.2222 | 3.02 | 3.0527 | 3.0067 | 2.925 | 2.7283 | 2.5067 | 2.39 | 2.3233 | 2.24 | 2.1983 | 2.14 | 2.1483 | 2.24 | 2.1417 | 2.1333 | 2.2833 | 2.4167 | 2.5833 | 2.6333 | 2.4917 | 2.3375 | 2.1908 | 2.0375 | 1.8917 | 1.7225 | 1.5733 | 1.49 | 1.21 | 0.97667 | 0.715 | 0.52333 | 0.43333 | 0.4625 | 0.48417 | 0.4775 | 0.43667 | 0.47667 | 0.5425 | 0.45167 | 0.55667 | 0.59583 | 0.61833 | 0.78333 | 0.81917 | 0.77167 | 0.755 | 0.80667

## Slide 48
Chart: Effluent total-Phosphorus (lb/day) Great Bend, Kansas
| Jan19 | F19 | M19 | A19 | M19 | J19 | July | A19 | S19 | O19 | N19 | D19 | Jan20 | F20 | M20 | A20 | M20 | J20 | July | A20 | S20 | O20 | N20 | D20 | Jan21 | F21 | M21 | A21 | M21 | J21 | July | A21 | S21 | O21 | N21 | D21 | Jan22 | F22 | M22 | A22 | M22 | J22 | July | A22 | S22 | O22 | N22 | D22
Actual | 28.2726 | 15.002 | 39.9891 | 30.441 | 23.819 | 23.9191 | 29.7721 | 24.2919 | 39.2539 | 29.9039 | 18.705 | 18.5473 | 19.1687 | 17.6666 | 17.8159 | 17.8343 | 21.4255 | 16.9769 | 20.7516 | 18.2171 | 6.7054 | 4.0195 | 1.6305 | 1.2013 | 3.9202 | 1.225 | 1.9764 | 11.3724 | 1.1034 | 0 | 0.9755 | 2.075 | 0.5895 | 5.8647 | 3.1025 | 0.8167 | 1.9606 | 3.3464 | 5.6945 | 1.3677 | 6.6086 | 2.2186 | 2.2772 | 16.9896 | 3.8026 | 5.685 | 3.4761 | 7.099
12-month average | 28.4796 | 28.4566 | 27.1111 | 28.2818 | 28.4618 | 29.0963 | 29.1448 | 29.4846 | 29.0765 | 28.1047 | 27.75 | 27.8884 | 26.8264 | 26.0678 | 26.2898 | 24.442 | 23.3915 | 23.192 | 22.6135 | 21.8618 | 21.3556 | 18.6432 | 16.4861 | 15.0633 | 13.6178 | 12.3471 | 10.9769 | 9.657 | 9.1185 | 7.425 | 6.0102 | 4.3622 | 3.017 | 2.5074 | 2.6612 | 2.7838 | 2.7518 | 2.5885 | 2.7653 | 3.0751 | 2.2414 | 2.7001 | 2.885 | 2.9935 | 4.2364 | 4.5042 | 4.4892 | 4.5203
Goal | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024 | 30.024

## Slide 49
Chart: Effluent total-Nitrogen (mg/L) Great Bend, Kansas
| Jan19 | F19 | M19 | A19 | M19 | J19 | July | A19 | S19 | O19 | N19 | D19 | Jan20 | F20 | M20 | A20 | M20 | J20 | July | A20 | S20 | O20 | N20 | D20 | Jan21 | F21 | M21 | A21 | M21 | J21 | July | A21 | S21 | O21 | N21 | D21 | Jan22 | F22 | M22 | A22 | M22 | J22 | July | A22 | S22 | O22 | N22 | D22
Monthly average tN | 8.7 | 7.3 | 11.4 | 5.9 | 5 | 7 | 3.63 | 8.6 | 13.9 | 14.6 | 13.8 | 12.2 | 14.9 | 12.5 | 12.4 | 11.5 | 9.9 | 5.5 | 12 | 13.7 | 13.1 | 9.5 | 5.8 | 5.9 | 9.7 | 9 | 7.5 | 12.27 | 4.6 | 6.6 | 4.9 | 4.6 | 6.3 | 6.4 | 2.62 | 3.4 | 9.2 | 8.9 | 14.2 | 8.4 | 8.9 | 5.7 | 4.2 | 3.2 | 0.97 | 5 | 4.9 | 5
Rolling AVG tN | 13.3978 | 12.788 | 12.6618 | 12.0983 | 11.7667 | 11.4133 | 10.9608 | 10.1442 | 9.7525 | 9.9275 | 9.7192 | 9.3358 | 9.8525 | 10.2858 | 10.3692 | 10.8358 | 11.2442 | 11.1192 | 11.8167 | 12.2417 | 12.175 | 11.75 | 11.0833 | 10.5583 | 10.125 | 9.8333 | 9.425 | 9.4892 | 9.0475 | 9.1392 | 8.5475 | 7.7892 | 7.2225 | 6.9642 | 6.6992 | 6.4908 | 6.4492 | 6.4408 | 6.9992 | 6.6767 | 7.035 | 6.96 | 6.9017 | 6.785 | 6.3408 | 6.2242 | 6.4142 | 6.5475

## Slide 50
Chart: Effluent total-Nitrogen (lb/day) Great Bend, Kansas
| Jan19 | F19 | M19 | A19 | M19 | J19 | July | A19 | S19 | O19 | N19 | D19 | Jan20 | F20 | M20 | A20 | M20 | J20 | July | A20 | S20 | O20 | N20 | D20 | Jan21 | F21 | M21 | A21 | M21 | J21 | July | A21 | S21 | O21 | N21 | D21 | Jan22 | F22 | M22 | A22 | M22 | J22 | July | A22 | S22 | O22 | N22 | D22
Actual | 98.3887 | 91.2621 | 136.434 | 71.8408 | 70.056 | 139.528 | 83.133 | 99.4812 | 188.147 | 161.702 | 122.918 | 107.751 | 109.851 | 96.0143 | 100.416 | 85.4558 | 60.6034 | 33.3475 | 75.4603 | 92.4347 | 73.2002 | 44.9234 | 27.8139 | 27.2601 | 44.7366 | 40.8326 | 36.1539 | 99.6712 | 36.254 | 48.1085 | 29.8731 | 23.8624 | 30.9472 | 31.2783 | 13.5475 | 15.4257 | 50.1034 | 39.7109 | 67.3855 | 37.0596 | 42.0119 | 26.9065 | 22.2428 | 24.3928 | 6.7064 | 45.1194 | 42.5824 | 44.3688
12-month average | 125.7723 | 122.7297 | 119.5829 | 121.1148 | 117.0087 | 118.3219 | 123.8091 | 125.8381 | 121.3401 | 115.6896 | 119.5477 | 120.8867 | 114.2202 | 115.1753 | 115.5714 | 112.5699 | 113.7044 | 112.9167 | 104.0683 | 103.429 | 102.8418 | 93.2628 | 83.5313 | 75.606 | 68.8984 | 63.4722 | 58.8737 | 53.5185 | 54.7032 | 52.674 | 53.9041 | 50.1052 | 44.3908 | 40.8697 | 39.7326 | 38.5438 | 37.5576 | 38.0048 | 37.9113 | 40.514 | 35.2963 | 35.7762 | 34.0093 | 33.3735 | 33.4177 | 31.3976 | 32.551 | 34.9706
Goal | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24 | 300.24

## Slide 51
Anoxic
Influent/RAS
Open Recycle Gate – Return Nitrates to Anoxic Zone
Oxic – Remove Ammonia
Before

## Slide 52
Anaerobic
Influent/RAS
Close Recycle Gate
Control D.O., Cycle
Oxic - Anoxic
Reduce Mixing
After

## Slide 53
VFA Production
PO4 Release
PAO Growth
Ammonia Conversion to Nitrates + Denitrification.
Luxury Phosphorus Uptake
After

## Slide 54: Colby, KS
Traditional newer activated sludge plant
Facing permit limits soon
Modified air levels and timing

## Slide 55
Before
Basic Activated Sludge
Some air control to denitrify & save energy
Influent/RAS
Ammonia to Nitrates

## Slide 56
After
Control air at influent
Cycle Air in Basin
Influent/RAS
Aerobic
Cycled Anoxic
Anaerobic
Aerobic
Cycled Anoxic

## Slide 57
After
Control air at influent
Cycle Air in Basin
Influent/RAS
Ammonia to Nitrates
VFA Production
PO4 Release
PAO Growth
Denitrification
Luxury Phosphorus Uptake

## Slide 58
Chart: Effluent total-Phosphorus (lb/day) Colby, Kansas
| Jan18 | F18 | M18 | A18 | M18 | J18 | July | A18 | S18 | O18 | N18 | D18 | Jan19 | F19 | M19 | A19 | M19 | J19 | July | A19 | S19 | O19 | N19 | D19 | Jan20 | F20 | M20 | A20 | M20 | J20 | July | A20 | S20 | O20 | N20 | D20 | Jan21 | F21 | M21 | A21 | M21 | J21 | July | A21 | S21 | O21 | N21 | D21 | Jan22 | F22 | M22 | A22 | M22 | J22 | July | A22 | S22 | O22 | N22 | D22
Actual | 12.4129 | 24.2534 | 12.6601 | 66.3197 | 38.6642 | 7.9063 | 20.9801 | 14.3865 | 14.2247 | 6.4677 | 5.4677 | 8.9121 | 15.0729 | 22.523 | 21.6823 | 21.4171 | 14.7234 | 22.2603 | 24.2844 | 16.4231 | 13.52 | 15.6875 | 16.248 | 19.1028 | 18.7884 | 21.2103 | 22.5313 | 72.8716 | 18.137 | 10.7686 | 1.4681 | 2.781 | 3.4911 | 3.2626 | 2.8543 | 2.7789 | 10.2932 | 35.7169 | 0.9688 | 1.877 | 48.4554 | 30.3659 | 22.0852 | 21.6823 | 17.127 | 5.4961 | 17.0762 | 15.7334 | 13.2406 | 15.9411 | 22.3279 | 19.7858 | 7.7262 | 12.3165 | 5.7463 | 2.4186 | 2.4244
12-month average | 0 | 0 | 0 | 0 | 12.4129 | 18.3331 | 16.4421 | 28.9115 | 30.8621 | 27.0361 | 26.171 | 24.6979 | 23.5342 | 21.8276 | 20.3403 | 19.388 | 19.6096 | 19.4654 | 20.2173 | 16.4754 | 14.4803 | 15.6765 | 15.9518 | 16.1216 | 16.0628 | 16.8312 | 17.7295 | 18.5787 | 18.8884 | 18.779 | 18.8497 | 23.1376 | 23.4221 | 22.4644 | 20.5631 | 19.4262 | 18.5905 | 17.5551 | 16.4389 | 15.0786 | 14.3707 | 15.5795 | 13.7827 | 7.8665 | 10.393 | 12.0261 | 13.7442 | 15.3193 | 16.4556 | 16.6418 | 17.8269 | 18.9065 | 19.1521 | 17.5041 | 19.284 | 20.7764 | 17.3823 | 15.8782 | 14.5166 | 12.9113
Goal | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412 | 9.8412

## Slide 59
Chart: Effluent total-Nitrogen (mg/L) Colby, Kansas
| Jan18 | F18 | M18 | A18 | M18 | J18 | July | A18 | S18 | O18 | N18 | D18 | Jan19 | F19 | M19 | A19 | M19 | J19 | July | A19 | S19 | O19 | N19 | D19 | Jan20 | F20 | M20 | A20 | M20 | J20 | July | A20 | S20 | O20 | N20 | D20 | Jan21 | F21 | M21 | A21 | M21 | J21 | July | A21 | S21 | O21 | N21 | D21 | Jan22 | F22 | M22 | A22 | M22 | J22 | July | A22 | S22 | O22 | N22 | D22
Monthly average tN | 2.46 | 7.9 | 4.89 | 8.9 | 15.9 | 5.4 | 8.6 | 6.8 | 7 | 5.1 | 9.9 | 2.6 | 4.4 | 4 | 3.8 | 3.8 | 3 | 8.8 | 3.54 | 3.6 | 5.41 | 22.5 | 4.8 | 7.5 | 9.3 | 18.5 | 15.6 | 10.3 | 4.67 | 5.8 | 2.04 | 10.6 | 11.8 | 14.2 | 10.6 | 7.86 | 9.1 | 10.8 | 15.1 | 2.94 | 4.6 | 16.4 | 5.2 | 16.6 | 10.5 | 6.4 | 15.2 | 20.1 | 14.5 | 6.6 | 15.1 | 3.8 | 7.9 | 7.1 | 8.1 | 4.7 | 4
Rolling AVG tN | 0 | 0 | 0 | 2.46 | 5.18 | 5.0833 | 6.0375 | 8.01 | 7.575 | 7.7214 | 7.6062 | 7.5389 | 7.295 | 7.5318 | 7.1208 | 7.2825 | 6.9575 | 6.8667 | 6.4417 | 5.3667 | 5.65 | 5.2283 | 4.9617 | 4.8292 | 6.2792 | 5.8542 | 6.2625 | 6.6708 | 7.8792 | 8.8625 | 9.4042 | 9.5433 | 9.2933 | 9.1683 | 9.7517 | 10.2842 | 9.5925 | 10.0758 | 10.1058 | 10.0892 | 9.4475 | 9.4058 | 8.7925 | 8.7867 | 9.67 | 9.9333 | 10.4333 | 10.325 | 9.675 | 10.0583 | 11.0783 | 11.5283 | 11.1783 | 11.1783 | 11.25 | 11.525 | 10.75 | 10.9917 | 10 | 9.4583

## Slide 60: Fine-Tuning a BNR Plant
Horton, KS Case Study

## Slide 61: Improve Biological Phosphorus Removal
New AeroMod plant -2023
Bio-P basin – bottom center
Mediocre phosphorus removal
Monitored ORP
Reduced mixing from 24/7 to 1 hour on, one hour off
Photo from Microsoft Maps.

## Slide 62: Results
Source: EPA ECHO Database

## Slide 63: Takeaways
Develop and execute total nitrogen strategy first
Once RAS is low in nitrates, can execute total phosphorus
Develop reasonable monitoring plan for nutrients and compliance

## Slide 64: Small Group Development
We are considering regular small-group meetings
Groups would be by plant type
i.e. SBR, oxidation ditch, Aeromod, etc.
Believe better sharing can help with nutrient removal efforts & plant management
i.e., contacts to help diagnose issues, share vendor information, etc.
We’ll ask for more input next week.

## Slide 65: KDHE Sponsored Technical Assistance
Available to all municipal plants in Kansas
Onsite – Willis
Remote – Weaver
No cost
Loaner equipment

## Slide 66: Contact Information & Technical Assistance
Free technical assistance on Nutrient Optimization in Kansas
Nicholas Willis
Environmental Finance Center at Wichita State University
nicholas.willis@wichita.edu
316-978-6538